## Slide 1
ECE 1710: Power Distribution Engineering and Smart Grids
Lecture 11
Dr. Robert Kerestes
University of Pittsburgh
Swanson School of Engineering
Department of Electrical and Computer Engineering
Notes: Instructions for editing school and department titles:
Select from menu: View > Master > Slide Master
Click on each text area you wish to edit. Text will become editable.

## Slide 2: Outline
Module #1: The modified line and approximate line segment models
Module #3: Modified ladder iterative technique
Module #3: Modified ladder iterative technique example
Outline of Lecture No. 11

## Slide 3
Learning Objectives:
  State the assumption made in the modified line model and why these assumptions can be justified
  Solve for voltage drops three-wire delta connected distribution lines
  Solve for ground current in three-phase distribution lines
  Produce an approximate phase impedance matrix using a sequence impedance matrix
  Solve for voltages and currents in a simple system with a transmission line given loading data
Learning Objectives

## Slide 4
Module #1
The modified line and approximate line segment models

## Slide 5: The Modified Line and Approximate Line Segment Models
Note that in Kersting’s book, he will sometimes refer to and use the modified line model i.e.
Module #1

## Slide 6: The Modified Line and Approximate Line Segment Models
We will not use the modified line model and will focus on the exact model. However, we will compare our results to the modified model so you should know what it consists of.
Module #1

## Slide 7: The Modified Line and Approximate Line Segment Models
Many times the only data available for a line segment will be the positive and zero sequence impedances as shown below:
Module #1

## Slide 8: The Modified Line and Approximate Line Segment Models
The approximate line model can be developed by applying the “reverse impedance transformation” from symmetrical component theory:
Module #1

## Slide 9: The Modified Line and Approximate Line Segment Models
We can then use Zapprox as being equivalent to Zabc and analysis can be peformed using the [a], [b], [c], [d], [A] and [B] matrices for the modified line model (since that is all the data we are given).
Module #1

## Slide 10: The Modified Line and Approximate Line Segment Models
Question: (True or False) We can get a good approximation of the phase impedance matrix if we only have sequence impedance data.
Module #1

## Slide 11: The Modified Line and Approximate Line Segment Models
Question: (True or False) The matrix [c] can be approximated to be essentially equal to zero regardless of how long the line is
Module #1

## Slide 12: Modified ladder iterative technique
Module #2

## Slide 13: The Modified Ladder Iterative Technique
Module #2
Previous example problems have assumed a linear system. Unfortunately, that will not be the usual case for distribution feeders.
When the source voltages are specified and the loads are specified as constant kW and kvar (constant PQ), the system becomes nonlinear, and an iterative method will have to be used to compute the load voltages and currents.
We will develop a simple form of the ladder iterative technique in order to demonstrate how the nonlinear system can be evaluated.

## Slide 14: The Modified Ladder Iterative Technique
The ladder technique is composed of two parts:
Forward sweep
Backward sweep
Module #2

## Slide 15: The Modified Ladder Iterative Technique
The forward sweep computes the downstream voltages from the source by applying:
To start the process, the load currents [Iabc]m are assumed to be equal to zero and the load voltages are computed. In the first iteration the load voltages will be the same as the source voltages.
Module #2

## Slide 16: The Modified Ladder Iterative Technique
The backward sweep computes the currents from the load back to the source using the most recently computed voltages from the forward sweep. The equation applied for this sweep is:
Module #2
Since this is the modified sweep, we can say , and hence

## Slide 17: The Modified Ladder Iterative Technique
After the first forward and backward sweeps, the new load voltages are computed using the most recent currents.
The forward and backward sweeps continue until the error between the new and previous load voltages is within a specified tolerance.
Module #2

## Slide 18: The Modified Ladder Iterative Technique
Modified ladder iterative algorithm flowchart
Module #2

## Slide 19
Modified ladder iterative algorithm Mathcad script
Module #2

## Slide 20: The Modified Ladder Iterative Technique
Question: In the ladder iterative technique we will continue to iterate until
The input current at node n and the output current at node m are equal to one another
Voltage unbalance at the receiving end of the line is within tolerance
The forward sweep and the backward sweep produce the same result
The old voltages and the new voltages for a given iteration are close enough to be considered “equal”
Module #2

## Slide 21: The Modified Ladder Iterative Technique
Question: The modified ladder iterative technique solves for
Receiving end power given initial load voltages and currents
Sending end power given initial load voltages and currents
Receiving end voltages given sending end voltages and receiving end power
Receiving end and currents given receiving end voltage and power
Module #2

## Slide 22
Module #3
Modified Ladder Iterative Technique Example

## Slide 23: Modified Ladder Iterative Technique Example
Module #3
Example: The line on the next slide serves an unbalanced three-phase load of
Phase a: 2500 kVA and PF = 0.9 lagging
Phase b: 2000 kVA and PF = 0.85 lagging
Phase c: 1500 kVA and PF = 0.95 lagging
The source voltages are balanced 12.47 kV.

## Slide 24: Modified Ladder Iterative Technique Example
Phase conductors:
336,400 26/7 ACSR
Neutral conductor:
4/0 6/1 ACSR
Module #3

## Slide 25: Modified Ladder Iterative Technique Example
Initializing the currents and voltages
Module #3

## Slide 26: Modified Ladder Iterative Technique Example
Initializing the load currents and voltages
Im_init =
0
0
0
Vlg_m_init =
0
0
0
Module #3

## Slide 27: Modified Ladder Iterative Technique Example
Calculating the forward sweep equation
Module #3

## Slide 28: Modified Ladder Iterative Technique Example
Forward sweep results. Source and load have about the same voltages on first pass:
abs(Vlg_m)
ans =
1.0e+03 *
7.1996
7.1996
7.1996
angle(Vlg_m)*180/pi
ans =
-0.0002
-120.0002
119.9998
Module #3

## Slide 29: Modified Ladder Iterative Technique Example
Then use the forward sweep voltage to update the load current using
where i represents the phase i.e. a, b, or c.
Module #3

## Slide 30: Modified Ladder Iterative Technique Example
The load currents are then:
abs(Im)
ans =
347.2407
277.7929
208.3445
angle(Im)*180/pi
ans =
-25.8421
-151.7886
101.8049
Module #3

## Slide 31: Modified Ladder Iterative Technique Example
Computing the error
Module #3

## Slide 32: Modified Ladder Iterative Technique Example
Error on first pass should be roughly equal to the source voltage:
error =
1.0e+03 *
7.1996
7.1996
7.1996
Module #3

## Slide 33: Modified Ladder Iterative Technique Example
Check if max error is less than tolerance, if so then exit and output, if no proceed to backward sweep
Module #3

## Slide 34: Modified Ladder Iterative Technique Example
Max error is greater than tolerance:
max(error)
ans =
7.1996e+03
tol =
1.0000e-03
Module #3

## Slide 35: Modified Ladder Iterative Technique Example
Calculate backward sweep equation
Module #3

## Slide 36: Modified Ladder Iterative Technique Example
Backwards sweep then calculates the source current
abs(In)
ans =
347.1845
277.7438
208.3214
angle(In)*180/pi
ans =
-25.8288
-151.7696
101.8281
Module #3

## Slide 37: Modified Ladder Iterative Technique Example
Return and perform the loop again.
Module #3

## Slide 38: Modified Ladder Iterative Technique Example
This continues until the max error is less than the tolerance:
Iteration | Max Error
1 | 7.1996e+03
2 | 466.2134
3 | 49.7729
4 | 4.7746
5 | 0.6473
6 | 0.0674
7 | 0.0097
8 | 0.0010
9 | 0.1505e-3
Module #3

## Slide 39: Modified Ladder Iterative Technique Example
Producing the final solution:
abs(Vlg_m)
ans =
1.0e+03 *
6.6781
6.9730
7.0555
angle(Vlg_m)*180/pi
ans =
-2.3274
-122.1311
118.7458
Module #3

## Slide 40: Modified Ladder Iterative Technique Example
Producing the final solution:
abs(Im)
ans =
374.3562
286.8193
212.6004
angle(Im)*180/pi
ans =
-28.1694
-153.9195
100.5509
Module #3