## Slide 1
ECE 1710: Power Distribution Engineering and Smart Grids
Lecture 15
Dr. Robert Kerestes
University of Pittsburgh
Swanson School of Engineering
Department of Electrical and Computer Engineering
Notes: Instructions for editing school and department titles:
Select from menu: View > Master > Slide Master
Click on each text area you wish to edit. Text will become editable.

## Slide 2: Outline
Module #1: Introduction to Three-Phase Transformers
Module #2: The Delta-Grounded Wye Step-Down Connection
Module #3: Use of Capacitors in Distribution Systems
Module #4: Loads in Distribution Systems
Outline of Lecture No. 15

## Slide 3
Learning Objectives:
  Model delta-wye transformers and use these models to perform forward-sweep, backward-sweep power flow analysis
  Model capacitors as inputs to a power flow solution
  Model constant power loads as inputs to a power flow solution
Learning Objectives

## Slide 4: Introduction to Three-Phase Transformers
Module #1

## Slide 5: Introduction to Three-Phase Transformers
Module #1
Three-phase transformer banks are found in the distribution substation, where the voltage is transformed from the transmission or subtransmission level to the distribution feeder level.
Substation transformer

## Slide 6: Introduction to Three-Phase Transformers
Module #1
Voltage regulation can be done with or without step regulators

## Slide 7: Introduction to Three-Phase Transformers
Module #1
Unique models of three-phase transformer banks applicable to radial distribution feeders exist. Models for the following three-phase connections are included:

## Slide 8: Introduction to Three-Phase Transformers
Module #1
The following figure defines the various voltages and currents for all three-phase transformer banks connected between the source-side node n and the load-side node m.

## Slide 9: Introduction to Three-Phase Transformers
Module #1
Delta-Wye connected transformer has a 30 degree phase shift associated
It is assumed that all variations of the wye–delta connections are connected in the “American Standard Thirty Degree” connection.
The described phase notation and the standard phase shifts for positive sequence voltages and currents are:

## Slide 10: Introduction to Three-Phase Transformers
Module #1
The models to be used in power-flow and short-circuit studies are generalized for the connections in the same form as have been developed for line segments and voltage regulators

## Slide 11: The Delta-Grounded Wye Step-Down Connection
Module #2

## Slide 12: The Delta-Grounded Wye Step-Down Connection
A delta-connected circuit and a wye connected circuit are shown below. We can connect transformer windings in the same way:
Delta
Wye
Module #2

## Slide 13: The Delta-Grounded Wye Step-Down Connection
Three single-phase transformers can be connected delta–grounded wye in a “standard 30 step-down connection” as shown below
Connection Diagram
Phasor Diagram
Module #2

## Slide 14: The Delta-Grounded Wye Step-Down Connection
Three single-phase transformers can be connected delta–grounded wye in a “standard 30 step-down connection” as shown below
Polarity mark
Module #2

## Slide 15: The Delta-Grounded Wye Step-Down Connection
Kirchhoff’s Voltage Law at no-load gives the line-to-line voltage between phases a and b as:
Module #2

## Slide 16: The Delta-Grounded Wye Step-Down Connection
The magnitude changes between the voltages can be defined in terms of the actual winding turns ratio (nt). These ratios are defined as follows:
Module #2

## Slide 17: The Delta-Grounded Wye Step-Down Connection
The line-to-line voltages on the primary side of the transformer connection as a function of the ideal secondary-side voltages are given by:
where:
Module #2

## Slide 18: The Delta-Grounded Wye Step-Down Connection
Recall that there is no line-to-neutral voltage on a delta connected circuit. However, what is needed is a relationship between “equivalent” line-to-neutral voltages at node n and the ideal secondary voltages.
This is provided in the following equation (derivation is left up to the student)
where:
Module #2

## Slide 19: The Delta-Grounded Wye Step-Down Connection
Recall that there is no line-to-neutral voltage on a delta connected circuit. However, what is needed is a relationship between “equivalent” line-to-neutral voltages at node n and the ideal secondary voltages.
This is provided in the following equation (derivation is left up to the student)
where:
Module #2

## Slide 20: The Delta-Grounded Wye Step-Down Connection
The ideal secondary voltages as a function of the secondary line-to-ground voltages and the secondary line currents are:
where
Module #2

## Slide 21: The Delta-Grounded Wye Step-Down Connection
Substituting:
where
Module #2

## Slide 22: The Delta-Grounded Wye Step-Down Connection
Substituting:
where
Module #2

## Slide 23: The Delta-Grounded Wye Step-Down Connection
The derivation of , and is left up to the student. These matrices are defined by
Module #2

## Slide 24: The Delta-Grounded Wye Step-Down Connection
Module #2
With this, we not have the forward sweep
and backward sweep

## Slide 25: The Delta-Grounded Wye Step-Down Connection
Module #2
With this, we not have the forward sweep
and backward sweep

## Slide 26: The Delta-Grounded Wye Step-Down Connection
Module #2
The current derivation will be left up to the student, but the resulting backward sweep equation is
where
and

## Slide 27
Module #3
Use of Capacitors in Distribution Systems

## Slide 28: Use of Capacitors in Distribution Systems
Module #3
Capacitors provide tremendous benefits to distribution system performance. Most noticeably, capacitors reduce losses, free up capacity, and reduce voltage
drop:
Losses; Capacity — By canceling the reactive power to motors and other loads with low power factor, capacitors decrease the line current. Reduced current frees up capacity; the same circuit can serve more load. Reduced current also significantly lowers the I2R line losses.
Voltage drop — Capacitors provide a voltage boost, which cancels part of the drop caused by system loads. Switched capacitors can regulate voltage on a circuit.

## Slide 29: Use of Capacitors in Distribution Systems
Module #3
Possible problems caused by capacitors:
If not properly applied or controlled, the reactive power from capacitor banks can create losses and high voltages.
The greatest danger of overvoltages occurs under light load. Good planning helps ensure that capacitors are sited properly.
More sophisticated controllers (like two-way radios with monitoring) reduce the risk of improperly controlling capacitors, compared to simple controllers (like a time clock).

## Slide 30: Use of Capacitors in Distribution Systems
Module #3
Capacitors work their magic by storing energy:
Capacitors are simple devices: two metal plates sandwiched around an insulating dielectric.
When charged to a given voltage, opposing charges fill the plates on either side of the dielectric.
The strong attraction of the charges across the very short distance separating them makes a tank of energy.
Capacitors oppose changes in voltage; it takes time to fill up the plates with charge, and once charged, it takes time to discharge the voltage.

## Slide 31: Use of Capacitors in Distribution Systems
Module #3
For ac power systems:
Capacitors do not store their energy very long i.e. just one-half cycle. Each half cycle, a capacitor charges up and then discharges its stored energy back into the system.
The net real power transfer is zero. Capacitors provide power just when reactive loads need it.
Capacitors and reactive loads exchange this reactive power back and forth. This benefits the system because that reactive power (and extra current) does not have to be transmitted from the generators all the way through many transformers and many miles of lines; the capacitors can provide the reactive power locally. This frees up the lines to carry real power, power that actually does work.

## Slide 32: Use of Capacitors in Distribution Systems
Module #3
The components of a distribution capacitor

## Slide 33: Use of Capacitors in Distribution Systems
Module #3
Pole mounted capacitor on overhead line

## Slide 34: Use of Capacitors in Distribution Systems
Module #3
More overhead line capacitors

## Slide 35: Use of Capacitors in Distribution Systems
Module #3
More overhead line capacitors

## Slide 36: Use of Capacitors in Distribution Systems
Module #3
Pad mounted capacitor

## Slide 37: Use of Capacitors in Distribution Systems
Module #3
Capacitor banks

## Slide 38: Use of Capacitors in Distribution Systems
Module #3
Capacitor banks with control circuitry

## Slide 39: Use of Capacitors in Distribution Systems
Module #3
Capacitor’s can be thought of as loads which absorb negative vars, or supply positive vars. The power absorbed by a capacitor is described by
where

## Slide 40: Use of Capacitors in Distribution Systems
Module #3
Therefore
which we can find the reactance of the capacitor by
and capacitance by

## Slide 41: Loads in Distribution Systems
Module #4

## Slide 42: Loads in Distribution Systems
Module #4
Loads in distribution systems can be quite complex to model. Load models include
Constant power (PQ) – watts and vars are constant
Constant impedance (Z) – ohms are constant
Constant current (I) - amps are constant
Combination (ZIP) – combination of any of 1-3
We will focus only on 1

## Slide 43: Loads in Distribution Systems
Module #4
Constant impedance loads can be
Single-phase
Two-phase
Three-phase
All can be connected in delta or wye, we will focus on wye

## Slide 44: Loads in Distribution Systems
Module #4
The notation for the specified complex powers and voltages are as follows:

## Slide 45: Loads in Distribution Systems
Module #4
The line currents for constant real and reactive power loads (PQ loads) are given by:
In this model, the line-to-neutral voltages will change during each iteration until convergence is achieved.