## Slide 1
ECE 1710: Power Distribution Engineering and Smart Grids
Lecture 9
Dr. Robert Kerestes
University of Pittsburgh
Swanson School of Engineering
Department of Electrical and Computer Engineering
Notes: Instructions for editing school and department titles:
Select from menu: View > Master > Slide Master
Click on each text area you wish to edit. Text will become editable.

## Slide 2: Outline
Module #1: Shunt Admittance of Overhead Lines
Module #2: Shunt Admittance of Concentric Neutral Underground Lines
Module #3: Shunt Admittance of Tape-Shielded Cable Underground Lines
Module #4: Sequence Admittance
Module #5: Shunt Admittance of Parallel Underground Lines
Outline of Lecture No. 9

## Slide 3
Learning Objectives:
  Calculate phase impedance and shunt admittance matrices using Kron reduction
  Write the matrix equation for voltage drop across a transmission line
Learning Objectives

## Slide 4: Series impedance of overhead lines
Module #1

## Slide 5: Shunt Impedance of Overhead Lines
Module #1
A charged conductor creates an electric field that emanates outward from the center of the conductor. Lines of equipotential are created that are concentric to the charged conductor.

## Slide 6: Shunt Impedance of Overhead Lines
Module #1
For an array of N positively charged conductors shown below, each having a unique charge density, q (C/m):

## Slide 7: Shunt Impedance of Overhead Lines
Where:
ε = ε0εr is the permittivity of the medium
ε0 is the permittivity of free space = 8.85 × 10−12 F/m
εr is the relative permittivity of the medium
qn is the charge density on conductor n (C/m)
Dni is the distance between conductor n and conductor i (ft)
Dnj is the distance between conductor n and conductor j (ft)
Dnn is the radius (RDn) of conductor n (ft)
Module #1

## Slide 8: Shunt Impedance of Overhead Lines
The method of conductors and their images is employed in the calculation of the shunt capacitance of overhead lines.
Module #1

## Slide 9: Shunt Impedance of Overhead Lines
We can derive the simplified voltage equation Assuming that
Module #1
We then have

## Slide 10: Shunt Impedance of Overhead Lines
Simplifying we have
Module #1
This gives the total voltage drop between conductor i and its image.

## Slide 11: Shunt Impedance of Overhead Lines
Where:
Sii is the distance from conductor i to its image i′ (ft)
Sij is the distance from conductor i to the image of conductor j (ft)
Dij is the distance from conductor i to conductor j (ft)
RDi is the radius of conductor i in (ft)
Module #1
The voltage drop between conductor i and the ground will be one-half of the drop between conductor and image i.e.

## Slide 12: Shunt Impedance of Overhead Lines
Now writing the self- and mutual-potential coefficients we have
Using air as the medium
Module #1

## Slide 13: Shunt Impedance of Overhead Lines
The self- and mutual- potential coefficients are defined as:
Module #1

## Slide 14: Shunt Impedance of Overhead Lines
And finally the primitive potential coefficient matrix is
and in partitioned form
Module #1

## Slide 15: Shunt Impedance of Overhead Lines
Using Kron reduction we then obtain the phase potential coefficient matrix
and then, inverting to obtain the phase capacitance matrix:
Module #1

## Slide 16: Shunt Impedance of Overhead Lines
Note that the same rules apply for V phase, single phase and delta connections as did with series impedances.
Finally, we can assume that the conductance to ground is zero because the medium is air. Therefore given use the admittance matrix
Module #1

## Slide 17: Shunt Impedance of Overhead Lines
Question: (True or false) only depends on the radius of the conductor and the distance from the conductor to its own image.
Module #1

## Slide 18: Shunt Impedance of Overhead Lines
Question: (True or false) only depends on the distance between conductor and and the distance from the conductor to its own image.
Module #1

## Slide 19: Series Impedance of Overhead Lines
Module #2
Shunt Admittance of Concentric Neutral Underground Lines

## Slide 20: Shunt Admittance of Concentric Neutral Underground Lines
Module #2
Most underground distribution lines consist of one or more concentric neutral cables.
The following definitions apply:
Rb = Radius of a circle passing through the centers of the neutral strands
dc = Diameter of the phase conductor
ds = Diameter of a neutral strand
k = Total number of neutral strands

## Slide 21
Module #2
The potential difference between a phase conductor and a neutral strand is given by:
See textbook for derivation
Shunt Admittance of Concentric Neutral Underground Lines

## Slide 22
Module #2
Because the neutral strands are all grounded, the previous equation gives the voltage drop between the phase conductor and ground. Therefore, the capacitance from the phase to ground for a concentric neutral cable is given by:
Shunt Admittance of Concentric Neutral Underground Lines

## Slide 23: Shunt Admittance of Concentric Neutral Underground Lines
Module #2
For this equation, ε = ε0εr = permittivity of the medium
ε0 = permittivity of free space = 0.01420 μF/mile
εr = relative permittivity of the medium

## Slide 24: Shunt Admittance of Concentric Neutral Underground Lines
Module #2
Cross-linked polyethylene (XLPE) is a very popular insulation material. If the minimum value of relative permittivity is assumed (2.3), the equation for the shunt admittance (at 60 Hz) of the concentric neutral cable is given by:

## Slide 25: Shunt Admittance of Concentric Neutral Underground Lines
Module #2
The mutual capacitance between lines can be considered to be zero, and the capacitance from concentric neutral to phase conductors can be considered zero. Thus the primitive or phase capacitance matrices are both diagonal.

## Slide 26: Shunt Admittance of Concentric Neutral Underground Lines
Module #2
Recall the example from lecture 8:
The cables are 15 kV, 250,000 CM stranded all aluminum with k = 13 strands of #14 annealed coated copper wires (1/3 neutral). The outside diameter of the cable over the neutral strands is 1.29 in. Determine the phase impedance matrix and the sequence impedance matrix. The insulation material is considered to be XLPE

## Slide 27: Shunt Admittance of Concentric Neutral Underground Lines
Module #2
Recall
Diameter of the 250,000 AA phase conductor = 0.567 in., so

## Slide 28: Shunt Admittance of Concentric Neutral Underground Lines
Module #2
Diameter of the #14 CU concentric neutral strand =0.0641 in., so
From phase a to ground we have:

## Slide 29: Shunt Admittance of Concentric Neutral Underground Lines
Module #2
Which gives us the shunt admittance matrix